ADDENDUM #1

FTFA20CB73, Renovate JSF Squadron Ops Hangar, Bldg 1412

06 April 2021

1. Sheet T-502, Rack Elevation Key Note #3 shall read as: “lockable wall mount cabinet equal to Model Number:EWMWG362425, 36x24x25,with Window Door and Gland Plate 19U, or approved equal”.

2. Sheet E-201: Keynote #7 shall read as “INSTALL RECEPTACLE IN RM 134 AND ROOM 141 for the new wall mount cabinets. the new wall mount cabinet in rm 134 is located on the plan right wall AS SHOWN IN T-401A”.

3. Sheet T-111, Key Note #6 shall read as “INSTALL NEW CABINET FOR EXISTING RED NETWORK EQUIPMENT. RELOCATE EXISTING RED NETWORK EQUIPMENT TO WALL MOUNT CABINET.”

4. T-002: Note “All new NIPR cabling and outlets shall be white instead of blue as called throughout the design” is added under “TELECOMMUNICATIONS GENERAL NOTES – FACILITY INFRASTRUCTURE:”

5. T-203/T-301: Note “All new NIPR cabling and outlets shall be white instead of blue as called throughout the design” is added.

6. Sheet T-002: Note “the contractor shall test all existing NIPR drops in the west SAPF (rooms 118-144) as shown to remain prior to starting demolition to have a record of condition” is added under “TELECOMMUNICATIONS GENERAL NOTES – FACILITY INFRASTRUCTURE:”.

7. Sheet A-120, General Notes:

Note 1 shall read as “CONSTRUCTION (PHASE I) SHALL START WITHIN FIVE (5) DAYS FROM NTP”.

Note 2 shall read as “CONSTRUCTION (PHASE II) SHALL START NO EARLIER THAN 1 NOVEMBER 2021 or after current occupants depart Eglin AFB, whichever date is later”.

Note 3 shall read as “ALL WORK IN ROOM 134/135 MUST BE COMPLETE WITHIN FORTY FIVE (45) DAYS FROM NTP”.

Note 4 shall read as “ALL WORK IN SUPPORT AND SUPPLY ROOMS, INCLUDING EXTERIOR CANOPY WORK MUST BE COMPLETE WITHIN SEVENTY FIVE (75) DAYS FROM NTP”.

8. Sheet T-502, Note: NOTE shall read as “ALL SIPR CABLES SHALL BE DISCONNECTED FROM EXISTING CABINET PULLED BACK, REROUTED, AND TERMINATED TO NEW PATCH PANEL IN CLASSIFIED WALL MOUNT CABINET. NO CLASSIFIED CABLING SHALL REMAIN IN THE EXISTING RACK”.

9. Sheet T-502, rack elevation NOTES: Key Note #1 shall read as “Existing HP FLOOR MOUNT lockable cabinet MUST BE REKEYED TO MEET 96 CS SECURITY REQUIREMENTS.”

10. Sheet T-501, Eglin Specific Rack Elevation Notes: Add an additional note and the note shall read as “These notes apply to all existing and new communications rack/cabinets in rooms 121, 134, 141, 434, 491, and 421 that are part of the scope of this project.”

11. Sheet E-200: Add keynote #4 and it shall read as “Install 2 new 208V/30A single phase circuits from panel C6 to the comm rack in room 491. These circuits will terminate in new L6-30R outlets.”

12. Sheet T-502: Add “EGLIN SPECIFIC RACK ELEVATION NOTES”. The notes shall read as:

* ALL TELECOMMUNICATION RACKS SHALL HAVE VERTICAL CABLE MANAGEMENT AND LADDER TRAY ABOVE EACH RACK. ALL TELECOMMUNICATION RACKS SHALL COMPLY WITH EGLIN RACK ELEVATION STANDARDS.
* These notes apply to all existing and new communications rack/cabinets in rooms 121, 134, 141, 434, 491, and 421 that are part of the scope of this project.

13. Sheet T-401:

 a. Detail 3 is deleted.

 b. Key Note #3 is deleted.

 b. Key Note #4 is deleted.

14. New drawing sheet T-401A is added to include the following:

 a. Detail 1 Server Room 134 Equipment Plan-Existing

 b. Detail 2 Server Room 134 Equipment Plan-New

c. Key Notes